## parameters
| version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.10.1 | TRUE | FALSE |  | 50 | 1

## bus
| name | vn_kv | type | zone | in_service
0 | Double Busbar 1 | 380 | b |  | TRUE
1 | Double Busbar 2 | 380 | b |  | TRUE
2 | Bus DB T0 | 380 | n |  | TRUE
3 | Bus DB T1 | 380 | n |  | TRUE
4 | Bus DB T2 | 380 | n |  | TRUE
5 | Bus DB T3 | 380 | n |  | TRUE
6 | Bus DB T4 | 380 | n |  | TRUE
7 | Bus DB T5 | 380 | n |  | TRUE
8 | Bus DB T6 | 380 | n |  | TRUE
9 | Bus DB T7 | 380 | n |  | TRUE
10 | Bus DB T8 | 380 | n |  | TRUE
11 | Bus DB T9 | 380 | n |  | TRUE
12 | Bus DB 1 | 380 | n |  | TRUE
13 | Bus DB 2 | 380 | n |  | TRUE
14 | Bus DB 3 | 380 | n |  | TRUE
15 | Bus DB 4 | 380 | n |  | TRUE
16 | Single Busbar | 110 | b |  | TRUE
17 | Bus SB 1 | 110 | n |  | TRUE
18 | Bus SB 2 | 110 | n |  | TRUE
19 | Bus SB 3 | 110 | n |  | TRUE
20 | Bus SB 4 | 110 | n |  | TRUE
21 | Bus SB 5 | 110 | n |  | TRUE
22 | Bus SB T1.1 | 110 | n |  | TRUE
23 | Bus SB T1.2 | 110 | n |  | TRUE
24 | Bus SB T2.1 | 110 | n |  | TRUE
25 | Bus SB T2.2 | 110 | n |  | TRUE
26 | Bus SB T3.1 | 110 | n |  | TRUE
27 | Bus SB T3.2 | 110 | n |  | TRUE
28 | Bus SB T4.1 | 110 | n |  | TRUE
29 | Bus SB T4.2 | 110 | n |  | TRUE
30 | Bus SB T5.1 | 110 | n |  | TRUE
31 | Bus SB T5.2 | 110 | n |  | TRUE
32 | Bus HV1 | 110 | n |  | TRUE
33 | Bus HV2 | 110 | n |  | TRUE
34 | Bus HV3 | 110 | n |  | TRUE
35 | Bus HV4 | 110 | n |  | TRUE
36 | Bus MV0 20kV | 20 | n |  | TRUE
37 | Bus MV0 | 10 | n |  | TRUE
38 | Bus MV1 | 10 | n |  | TRUE
39 | Bus MV2 | 10 | n |  | TRUE
40 | Bus MV3 | 10 | n |  | TRUE
41 | Bus MV4 | 10 | n |  | TRUE
42 | Bus MV5 | 10 | n |  | TRUE
43 | Bus MV6 | 10 | n |  | TRUE
44 | Bus MV7 | 10 | n |  | TRUE
45 | Bus LV0 | 0.4 | n |  | TRUE
46 | Bus LV1.1 | 0.4 | m |  | TRUE
47 | Bus LV1.2 | 0.4 | m |  | TRUE
48 | Bus LV1.3 | 0.4 | m |  | TRUE
49 | Bus LV1.4 | 0.4 | m |  | TRUE
50 | Bus LV1.5 | 0.4 | m |  | TRUE
51 | Bus LV2.1 | 0.4 | m |  | TRUE
52 | Bus LV2.2 | 0.4 | m |  | TRUE
53 | Bus LV2.3 | 0.4 | m |  | TRUE
54 | Bus LV2.4 | 0.4 | m |  | TRUE
55 | Bus LV2.2.1 | 0.4 | m |  | TRUE
56 | Bus LV2.2.2 | 0.4 | m |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MV Net 0 | 20 | 38 | 6 | 0 | 0 |  | 1 | TRUE | wye
1 | MV Net 1 | 32 | 38 | 6 | 0 | 0 |  | 1 | TRUE | wye
2 | MV Net 2 | 33 | 38 | 6 | 0 | 0 |  | 1 | TRUE | wye
3 | MV Net 3 | 34 | 38 | 6 | 0 | 0 |  | 1 | TRUE | wye
4 | MV Net 4 | 35 | 38 | 6 | 0 | 0 |  | 1 | TRUE | wye
5 | Further MV-Rings | 37 | 6 | 2 | 0 | 0 |  | 1 | TRUE | wye
6 | Industry Load | 36 | 18 | 4 | 0 | 0 |  | 1 | TRUE | wye
7 | LV Net 1 | 38 | 0.4 | 0.1 | 0 | 0 |  | 1 | TRUE | wye
8 | LV Net 2 | 39 | 0.4 | 0.06 | 0 | 0 |  | 1 | TRUE | wye
9 | LV Net 3 | 40 | 0.4 | 0.06 | 0 | 0 |  | 1 | TRUE | wye
10 | LV Net 5 | 42 | 0.4 | 0.06 | 0 | 0 |  | 1 | TRUE | wye
11 | LV Net 6 | 43 | 0.4 | 0.06 | 0 | 0 |  | 1 | TRUE | wye
12 | LV Net 7 | 44 | 0.4 | 0.06 | 0 | 0 |  | 1 | TRUE | wye
13 | Further LV-Feeders Load | 45 | 0.1 | 0.1 | 0 | 0 |  | 1 | TRUE | wye
14 | Residential Load | 46 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
15 | Residential Load(1) | 47 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
16 | Residential Load(2) | 48 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
17 | Residential Load(3) | 49 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
18 | Residential Load(4) | 50 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
19 | Rural Load | 51 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
20 | Rural Load(1) | 52 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
21 | Rural Load(2) | 53 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
22 | Rural Load(3) | 54 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
23 | Rural Load(4) | 55 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye
24 | Rural Load(5) | 56 | 0.01 | 0.03 | 0 | 0 |  | 1 | TRUE | wye

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source
0 | Wind Park | 21 | 20 | 4 | 45 | 1 | TRUE | WP | TRUE
1 | Biogas plant | 43 | 0.5 | 0 | 750 | 1 | TRUE | SGEN | TRUE
2 | Further MV Generator | 37 | 0.5 | 0.05 | 1000 | 1 | TRUE | SGEN | TRUE
3 | Industry Generator | 36 | 15 | 3 | 20000 | 1 | TRUE | SGEN | TRUE
4 | PV Park | 42 | 2 | 0.1 | 5000 | 1 | TRUE | PV | TRUE
5 | PV | 46 | 0.06 | 0 | 0.012 | 1 | TRUE | PV | TRUE
6 | PV(1) | 48 | 0.05 | 0 | 0.01 | 1 | TRUE | PV | TRUE
7 | PV(2) | 53 | 0.05 | 0 | 0.01 | 1 | TRUE | PV | TRUE
8 | PV(3) | 54 | 0.05 | 0 | 0.01 | 1 | TRUE | PV | TRUE
9 | PV(4) | 55 | 0.05 | 0 | 0.01 | 1 | TRUE | PV | TRUE
10 | PV(5) | 56 | 0.05 | 0 | 0.01 | 1 | TRUE | PV | TRUE

## gen
| name | bus | p_mw | vm_pu | sn_mva | min_q_mvar | max_q_mvar | scaling | slack | in_service | slack_weight | type | power_station_trafo
0 | Gas turbine | 35 | 100 | 1.03 |  |  |  | 1 | FALSE | TRUE | 0

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0 | 1 | 2 | b | DS | TRUE | DB DS0 | 0
1 | 0 | 3 | b | DS | TRUE | DB DS1 | 0
2 | 1 | 5 | b | DS | TRUE | DB DS2 | 0
3 | 0 | 5 | b | DS | FALSE | DB DS3 | 0
4 | 1 | 7 | b | DS | TRUE | DB DS4 | 0
5 | 0 | 7 | b | DS | FALSE | DB DS5 | 0
6 | 1 | 9 | b | DS | TRUE | DB DS6 | 0
7 | 0 | 9 | b | DS | FALSE | DB DS7 | 0
8 | 1 | 11 | b | DS | TRUE | DB DS8 | 0
9 | 0 | 11 | b | DS | FALSE | DB DS9 | 0
10 | 4 | 12 | b | DS | TRUE | DB DS10 | 0
11 | 6 | 13 | b | DS | TRUE | DB DS11 | 0
12 | 8 | 14 | b | DS | TRUE | DB DS12 | 0
13 | 10 | 15 | b | DS | TRUE | DB DS13 | 0
14 | 2 | 3 | b | CB | TRUE | DB CB0 | 0
15 | 5 | 4 | b | CB | TRUE | DB CB1 | 0
16 | 7 | 6 | b | CB | TRUE | DB CB2 | 0
17 | 9 | 8 | b | CB | TRUE | DB CB3 | 0
18 | 11 | 10 | b | CB | TRUE | DB CB4 | 0
19 | 22 | 17 | b | DS | TRUE | SB DS1.1 | 0
20 | 16 | 23 | b | DS | TRUE | SB DS1.2 | 0
21 | 24 | 18 | b | DS | TRUE | SB DS2.1 | 0
22 | 16 | 25 | b | DS | TRUE | SB DS2.2 | 0
23 | 26 | 19 | b | DS | TRUE | SB DS3.1 | 0
24 | 16 | 27 | b | DS | TRUE | SB DS3.2 | 0
25 | 28 | 20 | b | DS | TRUE | SB DS4.1 | 0
26 | 16 | 29 | b | DS | TRUE | SB DS4.2 | 0
27 | 30 | 21 | b | DS | TRUE | SB DS5.1 | 0
28 | 16 | 31 | b | DS | TRUE | SB DS5.2 | 0
29 | 23 | 22 | b | CB | TRUE | SB CB1 | 0
30 | 25 | 24 | b | CB | TRUE | SB CB2 | 0
31 | 27 | 26 | b | CB | TRUE | SB CB3 | 0
32 | 29 | 28 | b | CB | TRUE | SB CB4 | 0
33 | 31 | 30 | b | CB | TRUE | SB CB5 | 0
34 | 18 | 0 | l | LBS | TRUE | Switch Bus SB 2 - HV Line1 | 0
35 | 32 | 0 | l | LBS | TRUE | Switch Bus HV1 - HV Line1 | 0
36 | 32 | 1 | l | LBS | TRUE | Switch Bus HV1 - HV Line2 | 0
37 | 33 | 1 | l | LBS | TRUE | Switch Bus HV2 - HV Line2 | 0
38 | 33 | 2 | l | LBS | TRUE | Switch Bus HV2 - HV Line3 | 0
39 | 35 | 2 | l | LBS | TRUE | Switch Bus HV4 - HV Line3 | 0
40 | 32 | 3 | l | LBS | TRUE | Switch Bus HV1 - HV Line4 | 0
41 | 35 | 3 | l | LBS | TRUE | Switch Bus HV4 - HV Line4 | 0
42 | 34 | 4 | l | LBS | TRUE | Switch Bus HV3 - HV Line5 | 0
43 | 35 | 4 | l | LBS | TRUE | Switch Bus HV4 - HV Line5 | 0
44 | 19 | 5 | l | LBS | TRUE | Switch Bus SB 3 - HV Line6 | 0
45 | 34 | 5 | l | LBS | TRUE | Switch Bus HV3 - HV Line6 | 0
46 | 13 | 0 | t | LBS | TRUE | Switch DB2 - EHV-HV-Trafo | 0
47 | 17 | 0 | t | LBS | TRUE | Switch SB1 - EHV-HV-Trafo | 0
48 | 37 | 6 | l | LBS | TRUE | Switch Bus MV0 - MV Line1 | 0
49 | 38 | 6 | l | LBS | TRUE | Switch Bus MV1 - MV Line1 | 0
50 | 38 | 7 | l | LBS | TRUE | Switch Bus MV1 - MV Line2 | 0
51 | 39 | 7 | l | LBS | TRUE | Switch Bus MV2 - MV Line2 | 0
52 | 39 | 8 | l | LBS | TRUE | Switch Bus MV2 - MV Line3 | 0
53 | 40 | 8 | l | LBS | TRUE | Switch Bus MV3 - MV Line3 | 0
54 | 40 | 9 | l | LBS | TRUE | Switch Bus MV3 - MV Line4 | 0
55 | 41 | 9 | l | LBS | TRUE | Switch Bus MV4 - MV Line4 | 0
56 | 41 | 10 | l | LBS | TRUE | Switch Bus MV4 - MV Line5 | 0
57 | 42 | 10 | l | LBS | FALSE | Switch Bus MV5 - MV Line5 | 0
58 | 42 | 11 | l | LBS | TRUE | Switch Bus MV5 - MV Line6 | 0
59 | 43 | 11 | l | LBS | TRUE | Switch Bus MV6 - MV Line6 | 0
60 | 43 | 12 | l | LBS | TRUE | Switch Bus MV6 - MV Line7 | 0
61 | 44 | 12 | l | LBS | TRUE | Switch Bus MV7 - MV Line7 | 0
62 | 37 | 13 | l | LBS | TRUE | Switch Bus MV0 - MV Line8 | 0
63 | 44 | 13 | l | LBS | TRUE | Switch Bus MV7 - MV Line8 | 0
64 | 45 | 14 | l | LBS | TRUE | Switch Bus LV0 - LV Line1.1 | 0
65 | 46 | 14 | l | LBS | TRUE | Switch Bus LV1.1 - LV Line1.1 | 0
66 | 46 | 15 | l | LBS | TRUE | Switch Bus LV1.1 - LV Line1.2 | 0
67 | 47 | 15 | l | LBS | TRUE | Switch Bus LV1.2 - LV Line1.2 | 0
68 | 47 | 16 | l | LBS | TRUE | Switch Bus LV1.2 - LV Line1.3 | 0
69 | 48 | 16 | l | LBS | TRUE | Switch Bus LV1.3 - LV Line1.3 | 0
70 | 48 | 17 | l | LBS | TRUE | Switch Bus LV1.3 - LV Line1.4 | 0
71 | 49 | 17 | l | LBS | TRUE | Switch Bus LV1.4 - LV Line1.4 | 0
72 | 49 | 18 | l | LBS | TRUE | Switch Bus LV1.4 - LV Line1.6 | 0
73 | 50 | 18 | l | LBS | TRUE | Switch Bus LV1.5 - LV Line1.6 | 0
74 | 45 | 19 | l | LBS | TRUE | Switch Bus LV0 - LV Line2.1 | 0
75 | 51 | 19 | l | LBS | TRUE | Switch Bus LV2.1 - LV Line2.1 | 0
76 | 51 | 20 | l | LBS | TRUE | Switch Bus LV2.1 - LV Line2.2 | 0
77 | 52 | 20 | l | LBS | TRUE | Switch Bus LV2.2 - LV Line2.2 | 0
78 | 52 | 21 | l | LBS | TRUE | Switch Bus LV2.2 - LV Line2.3 | 0
79 | 53 | 21 | l | LBS | TRUE | Switch Bus LV2.3 - LV Line2.3 | 0
80 | 53 | 22 | l | LBS | TRUE | Switch Bus LV2.3 - LV Line2.4 | 0
81 | 54 | 22 | l | LBS | TRUE | Switch Bus LV2.4 - LV Line2.4 | 0
82 | 52 | 23 | l | LBS | TRUE | Switch Bus LV2.2 - LV Line2.2.1 | 0
83 | 55 | 23 | l | LBS | TRUE | Switch Bus LV2.2.1 - LV Line2.2.1 | 0
84 | 55 | 24 | l | LBS | TRUE | Switch Bus LV2.2.1 - LV Line2.2.2 | 0
85 | 56 | 24 | l | LBS | TRUE | Switch Bus LV2.2.2 - LV Line2.2.2 | 0
86 | 41 | 1 | t | LBS | TRUE | Switch MV4 - MV-LV-Trafo | 0
87 | 45 | 1 | t | LBS | TRUE | Switch LV0 - MV-LV-Trafo | 0

## shunt
| bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service
0 | 32 | Shunt | 0.96 | 0 | 110 | 1 | 1 | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | rx_min | rx_max
0 | External grid | 0 | 1.03 | 0 | 1 | TRUE | 10000 | 0.1 | 0.1

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | HV Line1 | 184-AL1/30-ST1A 110.0 | 18 | 32 | 30 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 1 | ol | TRUE
1 | HV Line2 | 184-AL1/30-ST1A 110.0 | 32 | 33 | 20 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 1 | ol | TRUE
2 | HV Line3 | 184-AL1/30-ST1A 110.0 | 33 | 35 | 30 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 1 | ol | TRUE
3 | HV Line4 | 184-AL1/30-ST1A 110.0 | 32 | 35 | 15 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 1 | ol | TRUE
4 | HV Line5 | 184-AL1/30-ST1A 110.0 | 34 | 35 | 25 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 1 | ol | TRUE
5 | HV Line6 | 184-AL1/30-ST1A 110.0 | 19 | 34 | 30 | 0.1571 | 0.4 | 8.8 | 0 | 0.535 | 1 | 2 | ol | TRUE
6 | MV Line1 | NA2XS2Y 1x185 RM/25 12/20 kV | 37 | 38 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
7 | MV Line2 | NA2XS2Y 1x185 RM/25 12/20 kV | 38 | 39 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
8 | MV Line3 | NA2XS2Y 1x185 RM/25 12/20 kV | 39 | 40 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
9 | MV Line4 | NA2XS2Y 1x185 RM/25 12/20 kV | 40 | 41 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
10 | MV Line5 | NA2XS2Y 1x185 RM/25 12/20 kV | 41 | 42 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
11 | MV Line6 | NA2XS2Y 1x185 RM/25 12/20 kV | 42 | 43 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
12 | MV Line7 | NA2XS2Y 1x185 RM/25 12/20 kV | 43 | 44 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
13 | MV Line8 | NA2XS2Y 1x185 RM/25 12/20 kV | 37 | 44 | 1.5 | 0.161 | 0.117 | 273 | 0 | 0.362 | 1 | 1 | cs | TRUE
14 | LV Line1.1 | NAYY 4x120 SE | 45 | 46 | 0.08 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
15 | LV Line1.2 | NAYY 4x120 SE | 46 | 47 | 0.08 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
16 | LV Line1.3 | NAYY 4x120 SE | 47 | 48 | 0.08 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
17 | LV Line1.4 | NAYY 4x120 SE | 48 | 49 | 0.08 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
18 | LV Line1.6 | NAYY 4x120 SE | 49 | 50 | 0.08 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
19 | LV Line2.1 | NAYY 4x120 SE | 45 | 51 | 0.12 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
20 | LV Line2.2 | NAYY 4x120 SE | 51 | 52 | 0.12 | 0.225 | 0.08 | 264 | 0 | 0.242 | 1 | 1 | cs | TRUE
21 | LV Line2.3 | 15-AL1/3-ST1A 0.4 | 52 | 53 | 0.12 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE
22 | LV Line2.4 | 15-AL1/3-ST1A 0.4 | 53 | 54 | 0.12 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE
23 | LV Line2.2.1 | 15-AL1/3-ST1A 0.4 | 52 | 55 | 0.12 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE
24 | LV Line2.2.2 | 15-AL1/3-ST1A 0.4 | 55 | 56 | 0.12 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | tp_pos
0 | EHV-HV-Trafo |  | 13 | 17 | 300 | 380 | 110 | 8 | 0.06 | 0 | 0 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE | 0
1 | MV-LV-Trafo |  | 41 | 45 | 0.4 | 10 | 0.4 | 4 | 1.325 | 0.95 | 0.2375 | 150 | hv | 0 | -2 | 2 | 2.5 |  | 0 | FALSE | 1 | 1 | TRUE | 0

## trafo3w
| name | std_type | hv_bus | mv_bus | lv_bus | sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_at_star_point | in_service | vk0_hv_percent | vk0_mv_percent | vk0_lv_percent | vkr0_hv_percent | vkr0_mv_percent | vkr0_lv_percent | vector_group
0 | HV-MV-MV-Trafo |  | 33 | 36 | 37 | 40 | 15 | 25 | 110 | 20 | 10 | 10.1 | 10.1 | 10.1 | 0.26667 | 0.033333 | 0.04 | 0 | 0 | 30 | 30 | hv | 0 | -8 | 8 | 1.25 |  | 0 | FALSE | TRUE

## impedance
| name | from_bus | to_bus | rft_pu | xft_pu | rtf_pu | xtf_pu | sn_mva | in_service
0 | Impedance | 34 | 32 | 0.074873 | 0.19887 | 0.074873 | 0.19887 | 100 | TRUE

## xward
| name | bus | ps_mw | qs_mvar | qz_mvar | pz_mw | r_ohm | x_ohm | vm_pu | slack_weight | in_service
0 | XWard 1 | 34 | 23.942 | -12.2419 | 0 | 2.8146 | 0 | 12.1895 | 1.0262 | 0 | TRUE
1 | XWard 2 | 32 | 3.776 | -7.77 | 0 | 9.1749 | 0 | 50.5622 | 1.024 | 0 | TRUE

## bus_geodata
| x | y | coords
0 | 2.2615 | 0.41434
1 | 2.2722 | 0.31992
2 | 1.9871 | 0.50733
3 | 2.0543 | 0.69849
4 | 2.3459 | 1.0556
5 | 2.3204 | 0.71239
6 | 1.7299 | -0.044033
7 | 2.0054 | 0.14946
8 | 2.8538 | 0.58718
9 | 2.5598 | 0.45748
10 | 2.7791 | -0.043923
11 | 2.4926 | 0.12987
12 | 2.4196 | 1.3582
13 | 1.4854 | -0.25376
14 | 3.1378 | 0.70672
15 | 3.07 | -0.17252
16 | 0.47303 | -1.1404
17 | 1.2302 | -0.44778
18 | -0.46622 | -0.70056
19 | -0.43632 | -1.4355
20 | 0.59339 | -2.1779
21 | 1.0971 | -1.9017
22 | 0.9693 | -0.65022
23 | 0.71542 | -0.86978
24 | -0.12901 | -0.77392
25 | 0.19521 | -0.91261
26 | -0.10973 | -1.4266
27 | 0.20063 | -1.2884
28 | 0.53263 | -1.8478
29 | 0.49692 | -1.4972
30 | 0.95237 | -1.6111
31 | 0.73688 | -1.3357
32 | -0.80075 | -0.77114
33 | -1.1316 | -0.8428
34 | -0.74065 | -1.324
35 | -0.92321 | -1.0491
36 | -1.3055 | -1.1598
37 | -1.4036 | -0.64365
38 | -1.7444 | -0.72351
39 | -2.0489 | -0.58717
40 | -2.281 | -0.34166
41 | -2.3827 | -0.018167
42 | -2.0511 | 0.039833
43 | -1.7388 | -0.075612
44 | -1.4987 | -0.31599
45 | -2.6923 | 0.15454
46 | -2.9967 | -0.027671
47 | -3.2882 | -0.17422
48 | -3.5791 | -0.29327
49 | -3.8754 | -0.37858
50 | -4.1866 | -0.38381
51 | -2.767 | 0.4981
52 | -2.8802 | 0.82119
53 | -3.1909 | 0.9272
54 | -3.4144 | 1.1513
55 | -2.7834 | 1.151
56 | -2.829 | 1.4742

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 1.03 | 0 | -120.554 | 8.5583
1 | 1.03 | 0 | 0 | 0
2 | 1.03 | 0 | 0 | 0
3 | 1.03 | 0 | 0 | 0
4 | 1.03 | 0 | 0 | 0
5 | 1.03 | 0 | 0 | 0
6 | 1.03 | 0 | 0 | 0
7 | 1.03 | 0 | 0 | 0
8 | 1.03 | 0 | 0 | 0
9 | 1.03 | 0 | 0 | 0
10 | 1.03 | 0 | 0 | 0
11 | 1.03 | 0 | 0 | 0
12 | 1.03 | 0 | 0 | 0
13 | 1.03 | 0 | 0 | 0
14 | 1.03 | 0 | 0 | 0
15 | 1.03 | 0 | 0 | 0
16 | 1.0325 | -1.7332 | 0 | 0
17 | 1.0325 | -1.7332 | 0 | 0
18 | 1.0325 | -1.7332 | 0 | 0
19 | 1.0325 | -1.7332 | 0 | 0
20 | 1.0325 | -1.7332 | 38 | 6
21 | 1.0325 | -1.7332 | -20 | -4
22 | 1.0325 | -1.7332 | 0 | 0
23 | 1.0325 | -1.7332 | 0 | 0
24 | 1.0325 | -1.7332 | 0 | 0
25 | 1.0325 | -1.7332 | 0 | 0
26 | 1.0325 | -1.7332 | 0 | 0
27 | 1.0325 | -1.7332 | 0 | 0
28 | 1.0325 | -1.7332 | 0 | 0
29 | 1.0325 | -1.7332 | 0 | 0
30 | 1.0325 | -1.7332 | 0 | 0
31 | 1.0325 | -1.7332 | 0 | 0
32 | 1.0217 | -3.9453 | 51.3526 | -1.3409
33 | 1.0142 | -4.6062 | 38 | 6
34 | 1.0255 | -3.5162 | 64.9017 | -6.9613
35 | 1.03 | -3.2593 | -62 | -14.299
36 | 1.0007 | -36.3384 | 3 | 1
37 | 1.0008 | -36.1689 | 5.5 | 1.95
38 | 0.99687 | -36.1989 | 0.4 | 0.1
39 | 0.99406 | -36.2007 | 0.4 | 0.06
40 | 0.99231 | -36.1684 | 0.4 | 0.06
41 | 0.99161 | -36.1018 | 0 | 0
42 | 1.0117 | -35.7118 | -1.6 | -0.04
43 | 1.0078 | -35.8633 | -0.1 | 0.06
44 | 1.0038 | -36.0323 | 0.4 | 0.06
45 | 0.94893 | 175.0616 | 0.1 | 0.1
46 | 0.94903 | 176.288 | -0.05 | 0.03
47 | 0.9448 | 177.1762 | 0.01 | 0.03
48 | 0.94321 | 177.8786 | -0.04 | 0.03
49 | 0.93821 | 178.2638 | 0.01 | 0.03
50 | 0.93572 | 178.458 | 0.01 | 0.03
51 | 0.95439 | 177.4602 | 0.01 | 0.03
52 | 0.96498 | 179.5412 | 0.01 | 0.03
53 | 1.048 | -174.4732 | -0.04 | 0.03
54 | 1.0913 | -171.8307 | -0.04 | 0.03
55 | 1.048 | -174.4732 | -0.04 | 0.03
56 | 1.0913 | -171.8307 | -0.04 | 0.03

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 39.6615 | -4.0797 | -39.0821 | 4.4963 | 0.57938 | 0.41657 | 0.20269 | 0.2021 | 0.20269 | 1.0325 | -1.7332 | 1.0217 | -3.9453 | 37.8858
1 | 19.6325 | 3.6143 | -19.5327 | -4.0534 | 0.099795 | -0.43913 | 0.10255 | 0.10324 | 0.10324 | 1.0217 | -3.9453 | 1.0142 | -4.6062 | 19.2974
2 | -26.8586 | -5.8642 | 27.1426 | 5.5389 | 0.28402 | -0.32528 | 0.14228 | 0.14116 | 0.14228 | 1.0142 | -4.6062 | 1.03 | -3.2593 | 26.5936
3 | -27.8093 | -6.3758 | 27.9605 | 6.2329 | 0.15127 | -0.14288 | 0.14657 | 0.14598 | 0.14657 | 1.0217 | -3.9453 | 1.03 | -3.2593 | 27.3969
4 | -6.8796 | -3.3665 | 6.8968 | 2.5271 | 0.017253 | -0.83938 | 0.039202 | 0.03743 | 0.039202 | 1.0255 | -3.5162 | 1.03 | -3.2593 | 7.3275
5 | 62.8651 | -10.15 | -62.128 | 9.9017 | 0.7371 | -0.24827 | 0.32372 | 0.32201 | 0.32372 | 1.0325 | -1.7332 | 1.0255 | -3.5162 | 30.2545
6 | 1.1688 | 0.62655 | -1.1646 | -0.63629 | 0.0042602 | -0.009739 | 0.076506 | 0.076859 | 0.076859 | 1.0008 | -36.1689 | 0.99687 | -36.1989 | 21.2318
7 | 0.76458 | 0.53629 | -0.76245 | -0.54749 | 0.0021364 | -0.011196 | 0.054089 | 0.054517 | 0.054517 | 0.99687 | -36.1989 | 0.99406 | -36.2007 | 15.0599
8 | 0.36245 | 0.48749 | -0.36153 | -0.49951 | 0.00091709 | -0.012024 | 0.035281 | 0.035876 | 0.035876 | 0.99406 | -36.2007 | 0.99231 | -36.1684 | 9.9106
9 | -0.038471 | 0.43951 | 0.038962 | -0.45181 | 0.00049115 | -0.012302 | 0.02567 | 0.026404 | 0.026404 | 0.99231 | -36.1684 | 0.99161 | -36.1018 | 7.2938
10 | 9.8256e-08 | -0.01265 | -4.5543e-14 | 3.3214e-14 | 9.8256e-08 | -0.01265 | 0.00073653 | 3.2819e-15 | 0.00073653 | 0.99161 | -36.1018 | 0.99163 | -36.1027 | 0.20346
11 | 1.6 | 0.04 | -1.594 | -0.048725 | 0.0060449 | -0.0087251 | 0.091333 | 0.091354 | 0.091354 | 1.0117 | -35.7118 | 1.0078 | -35.8633 | 25.2359
12 | 1.694 | -0.011275 | -1.6871 | 0.0032179 | 0.0068225 | -0.008057 | 0.097042 | 0.097039 | 0.097042 | 1.0078 | -35.8633 | 1.0038 | -36.0323 | 26.8071
13 | -1.2832 | 0.053185 | 1.2871 | -0.063218 | 0.0039785 | -0.010033 | 0.074087 | 0.074121 | 0.074121 | 1.0008 | -36.1689 | 1.0038 | -36.0323 | 20.4754
14 | -0.053184 | 0.15242 | 0.05644 | -0.15126 | 0.0032558 | 0.0011567 | 0.24555 | 0.24555 | 0.24555 | 0.94893 | 175.0616 | 0.94903 | 176.288 | 101.4656
15 | -0.0064402 | 0.12126 | 0.0082821 | -0.12061 | 0.0018419 | 0.00065395 | 0.18469 | 0.18469 | 0.18469 | 0.94903 | 176.288 | 0.9448 | 177.1762 | 76.3174
16 | -0.018282 | 0.090608 | 0.019359 | -0.090226 | 0.0010768 | 0.00038192 | 0.14121 | 0.14121 | 0.14121 | 0.9448 | 177.1762 | 0.94321 | 177.8786 | 58.3529
17 | 0.020641 | 0.060226 | -0.020128 | -0.060045 | 0.00051256 | 0.0001813 | 0.097426 | 0.097427 | 0.097427 | 0.94321 | 177.8786 | 0.93821 | 178.2638 | 40.2591
18 | 0.010128 | 0.030045 | -0.01 | -0.03 | 0.00012848 | 4.4751e-05 | 0.048778 | 0.048779 | 0.048779 | 0.93821 | 178.2638 | 0.93572 | 178.458 | 20.1566
19 | -0.093992 | 0.19119 | 0.1025 | -0.18817 | 0.0085062 | 0.003023 | 0.32406 | 0.32406 | 0.32406 | 0.94893 | 175.0616 | 0.95439 | 177.4602 | 133.9093
20 | -0.1125 | 0.15817 | 0.11948 | -0.15569 | 0.0069796 | 0.0024802 | 0.29354 | 0.29355 | 0.29355 | 0.95439 | 177.4602 | 0.96498 | 179.5412 | 121.2998
21 | -0.064739 | 0.062846 | 0.077045 | -0.060551 | 0.012306 | 0.0022948 | 0.13496 | 0.13496 | 0.13496 | 0.96498 | 179.5412 | 1.048 | -174.4732 | 128.5297
22 | -0.037045 | 0.030551 | 0.04 | -0.03 | 0.002955 | 0.00055096 | 0.066131 | 0.066131 | 0.066131 | 1.048 | -174.4732 | 1.0913 | -171.8307 | 62.9819
23 | -0.064739 | 0.062846 | 0.077045 | -0.060551 | 0.012306 | 0.0022948 | 0.13496 | 0.13496 | 0.13496 | 0.96498 | 179.5412 | 1.048 | -174.4732 | 128.5297
24 | -0.037045 | 0.030551 | 0.04 | -0.03 | 0.002955 | 0.00055096 | 0.066131 | 0.066131 | 0.066131 | 1.048 | -174.4732 | 1.0913 | -171.8307 | 62.9819

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 120.554 | -8.5583 | -120.5265 | 12.2297 | 0.027536 | 3.6714 | 0.17828 | 0.61586 | 1.03 | 0 | 1.0325 | -1.7332 | 39.1124
1 | -0.038962 | 0.46446 | 0.047176 | -0.44361 | 0.008214 | 0.02085 | 0.027138 | 0.67856 | 0.99161 | -36.1018 | 0.94893 | 175.0616 | 117.5307

## res_trafo3w
| p_hv_mw | q_hv_mvar | p_mv_mw | q_mv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_mv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_mv_pu | va_mv_degree | vm_lv_pu | va_lv_degree | va_internal_degree | vm_internal_pu | loading_percent
0 | 8.3913 | 3.9176 | -3 | -1 | -5.3857 | -2.6297 | 0.0055684 | 0.28787 | 0.047927 | 0.091222 | 0.34575 | 1.0142 | -4.6062 | 1.0007 | -36.3384 | 1.0008 | -36.1689 | -5.5389 | 1.0058 | 23.9546

## res_impedance
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka
0 | 4.1059 | 0.42611 | -4.0937 | -0.39388 | 0.012133 | 0.032226 | 0.021128 | 0.021128

## res_ext_grid
| p_mw | q_mvar
0 | 120.554 | -8.5583

## res_load
| p_mw | q_mvar
0 | 38 | 6
1 | 38 | 6
2 | 38 | 6
3 | 38 | 6
4 | 38 | 6
5 | 6 | 2
6 | 18 | 4
7 | 0.4 | 0.1
8 | 0.4 | 0.06
9 | 0.4 | 0.06
10 | 0.4 | 0.06
11 | 0.4 | 0.06
12 | 0.4 | 0.06
13 | 0.1 | 0.1
14 | 0.01 | 0.03
15 | 0.01 | 0.03
16 | 0.01 | 0.03
17 | 0.01 | 0.03
18 | 0.01 | 0.03
19 | 0.01 | 0.03
20 | 0.01 | 0.03
21 | 0.01 | 0.03
22 | 0.01 | 0.03
23 | 0.01 | 0.03
24 | 0.01 | 0.03

## res_sgen
| p_mw | q_mvar
0 | 20 | 4
1 | 0.5 | 0
2 | 0.5 | 0.05
3 | 15 | 3
4 | 2 | 0.1
5 | 0.06 | 0
6 | 0.05 | 0
7 | 0.05 | 0
8 | 0.05 | 0
9 | 0.05 | 0
10 | 0.05 | 0

## res_shunt
| p_mw | q_mvar | vm_pu
0 | 0 | 1.002 | 1.0217

## res_gen
| p_mw | q_mvar | va_degree | vm_pu
0 | 100 | 20.299 | -3.2593 | 1.03

## res_xward
| p_mw | q_mvar | vm_pu | va_internal_degree | vm_internal_pu
0 | 26.9017 | -12.9613 | 1.0255 | -3.5162 | 1.0262
1 | 13.3526 | -8.3429 | 1.0217 | -3.9453 | 1.024

## res_switch
| i_ka | loading_percent
0
1
2
3 | 0
4
5 | 0
6
7 | 0
8
9 | 0
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34 | 0.20269
35 | 0.20269
36 | 0.10324
37 | 0.10324
38 | 0.14228
39 | 0.14228
40 | 0.14657
41 | 0.14657
42 | 0.039202
43 | 0.039202
44 | 0.32372
45 | 0.32372
46 | 0.17828
47 | 0.61586
48 | 0.076859
49 | 0.076859
50 | 0.054517
51 | 0.054517
52 | 0.035876
53 | 0.035876
54 | 0.026404
55 | 0.026404
56 | 0.00073653
57 | 0
58 | 0.091354
59 | 0.091354
60 | 0.097042
61 | 0.097042
62 | 0.074121
63 | 0.074121
64 | 0.24555
65 | 0.24555
66 | 0.18469
67 | 0.18469
68 | 0.14121
69 | 0.14121
70 | 0.097427
71 | 0.097427
72 | 0.048779
73 | 0.048779
74 | 0.32406
75 | 0.32406
76 | 0.29355
77 | 0.29355
78 | 0.13496
79 | 0.13496
80 | 0.066131
81 | 0.066131
82 | 0.13496
83 | 0.13496
84 | 0.066131
85 | 0.066131
86 | 0.027138
87 | 0.67856

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | sgen | name | object
16 | sgen | bus | int64
17 | sgen | p_mw | float64
18 | sgen | q_mvar | float64
19 | sgen | sn_mva | float64
20 | sgen | scaling | float64
21 | sgen | in_service | bool
22 | sgen | type | object
23 | sgen | current_source | bool
24 | gen | name | object
25 | gen | bus | uint32
26 | gen | p_mw | float64
27 | gen | vm_pu | float64
28 | gen | sn_mva | float64
29 | gen | min_q_mvar | float64
30 | gen | max_q_mvar | float64
31 | gen | scaling | float64
32 | gen | slack | bool
33 | gen | in_service | bool
34 | gen | slack_weight | float64
35 | gen | type | object
36 | gen | power_station_trafo | float64
37 | switch | bus | int64
38 | switch | element | int64
39 | switch | et | object
40 | switch | type | object
41 | switch | closed | bool
42 | switch | name | object
43 | switch | z_ohm | float64
44 | switch | in_ka | float64
45 | shunt | bus | uint32
46 | shunt | name | object
47 | shunt | q_mvar | float64
48 | shunt | p_mw | float64
49 | shunt | vn_kv | float64
50 | shunt | step | uint32
51 | shunt | max_step | uint32
52 | shunt | in_service | bool
53 | ext_grid | name | object
54 | ext_grid | bus | uint32
55 | ext_grid | vm_pu | float64
56 | ext_grid | va_degree | float64
57 | ext_grid | slack_weight | float64
58 | ext_grid | in_service | bool
59 | ext_grid | s_sc_max_mva | float64
60 | ext_grid | rx_min | float64
61 | ext_grid | rx_max | float64
62 | line | name | object
63 | line | std_type | object
64 | line | from_bus | uint32
65 | line | to_bus | uint32
66 | line | length_km | float64
67 | line | r_ohm_per_km | float64
68 | line | x_ohm_per_km | float64
69 | line | c_nf_per_km | float64
70 | line | g_us_per_km | float64
71 | line | max_i_ka | float64
72 | line | df | float64
73 | line | parallel | uint32
74 | line | type | object
75 | line | in_service | bool
76 | trafo | name | object
77 | trafo | std_type | object
78 | trafo | hv_bus | uint32
79 | trafo | lv_bus | uint32
80 | trafo | sn_mva | float64
81 | trafo | vn_hv_kv | float64
82 | trafo | vn_lv_kv | float64
83 | trafo | vk_percent | float64
84 | trafo | vkr_percent | float64
85 | trafo | pfe_kw | float64
86 | trafo | i0_percent | float64
87 | trafo | shift_degree | float64
88 | trafo | tap_side | object
89 | trafo | tap_neutral | float64
90 | trafo | tap_min | float64
91 | trafo | tap_max | float64
92 | trafo | tap_step_percent | float64
93 | trafo | tap_step_degree | float64
94 | trafo | tap_pos | float64
95 | trafo | tap_phase_shifter | bool
96 | trafo | parallel | uint32
97 | trafo | df | float64
98 | trafo | in_service | bool
99 | trafo | tp_pos | float64
100 | trafo3w | name | object
101 | trafo3w | std_type | object
102 | trafo3w | hv_bus | uint32
103 | trafo3w | mv_bus | uint32
104 | trafo3w | lv_bus | uint32
105 | trafo3w | sn_hv_mva | float64
106 | trafo3w | sn_mv_mva | float64
107 | trafo3w | sn_lv_mva | float64
108 | trafo3w | vn_hv_kv | float64
109 | trafo3w | vn_mv_kv | float64
110 | trafo3w | vn_lv_kv | float64
111 | trafo3w | vk_hv_percent | float64
112 | trafo3w | vk_mv_percent | float64
113 | trafo3w | vk_lv_percent | float64
114 | trafo3w | vkr_hv_percent | float64
115 | trafo3w | vkr_mv_percent | float64
116 | trafo3w | vkr_lv_percent | float64
117 | trafo3w | pfe_kw | float64
118 | trafo3w | i0_percent | float64
119 | trafo3w | shift_mv_degree | float64
120 | trafo3w | shift_lv_degree | float64
121 | trafo3w | tap_side | object
122 | trafo3w | tap_neutral | int32
123 | trafo3w | tap_min | int32
124 | trafo3w | tap_max | int32
125 | trafo3w | tap_step_percent | float64
126 | trafo3w | tap_step_degree | float64
127 | trafo3w | tap_pos | int32
128 | trafo3w | tap_at_star_point | bool
129 | trafo3w | in_service | bool
130 | trafo3w | vk0_hv_percent | float64
131 | trafo3w | vk0_mv_percent | float64
132 | trafo3w | vk0_lv_percent | float64
133 | trafo3w | vkr0_hv_percent | float64
134 | trafo3w | vkr0_mv_percent | float64
135 | trafo3w | vkr0_lv_percent | float64
136 | trafo3w | vector_group | float64
137 | impedance | name | object
138 | impedance | from_bus | uint32
139 | impedance | to_bus | uint32
140 | impedance | rft_pu | float64
141 | impedance | xft_pu | float64
142 | impedance | rtf_pu | float64
143 | impedance | xtf_pu | float64
144 | impedance | sn_mva | float64
145 | impedance | in_service | bool
146 | xward | name | object
147 | xward | bus | uint32
148 | xward | ps_mw | float64
149 | xward | qs_mvar | float64
150 | xward | qz_mvar | float64
151 | xward | pz_mw | float64
152 | xward | r_ohm | float64
153 | xward | x_ohm | float64
154 | xward | vm_pu | float64
155 | xward | slack_weight | float64
156 | xward | in_service | bool
157 | bus_geodata | x | float64
158 | bus_geodata | y | float64
159 | bus_geodata | coords | object
160 | res_bus | vm_pu | float64
161 | res_bus | va_degree | float64
162 | res_bus | p_mw | float64
163 | res_bus | q_mvar | float64
164 | res_line | p_from_mw | float64
165 | res_line | q_from_mvar | float64
166 | res_line | p_to_mw | float64
167 | res_line | q_to_mvar | float64
168 | res_line | pl_mw | float64
169 | res_line | ql_mvar | float64
170 | res_line | i_from_ka | float64
171 | res_line | i_to_ka | float64
172 | res_line | i_ka | float64
173 | res_line | vm_from_pu | float64
174 | res_line | va_from_degree | float64
175 | res_line | vm_to_pu | float64
176 | res_line | va_to_degree | float64
177 | res_line | loading_percent | float64
178 | res_trafo | p_hv_mw | float64
179 | res_trafo | q_hv_mvar | float64
180 | res_trafo | p_lv_mw | float64
181 | res_trafo | q_lv_mvar | float64
182 | res_trafo | pl_mw | float64
183 | res_trafo | ql_mvar | float64
184 | res_trafo | i_hv_ka | float64
185 | res_trafo | i_lv_ka | float64
186 | res_trafo | vm_hv_pu | float64
187 | res_trafo | va_hv_degree | float64
188 | res_trafo | vm_lv_pu | float64
189 | res_trafo | va_lv_degree | float64
190 | res_trafo | loading_percent | float64
191 | res_trafo3w | p_hv_mw | float64
192 | res_trafo3w | q_hv_mvar | float64
193 | res_trafo3w | p_mv_mw | float64
194 | res_trafo3w | q_mv_mvar | float64
195 | res_trafo3w | p_lv_mw | float64
196 | res_trafo3w | q_lv_mvar | float64
197 | res_trafo3w | pl_mw | float64
198 | res_trafo3w | ql_mvar | float64
199 | res_trafo3w | i_hv_ka | float64
200 | res_trafo3w | i_mv_ka | float64
201 | res_trafo3w | i_lv_ka | float64
202 | res_trafo3w | vm_hv_pu | float64
203 | res_trafo3w | va_hv_degree | float64
204 | res_trafo3w | vm_mv_pu | float64
205 | res_trafo3w | va_mv_degree | float64
206 | res_trafo3w | vm_lv_pu | float64
207 | res_trafo3w | va_lv_degree | float64
208 | res_trafo3w | va_internal_degree | float64
209 | res_trafo3w | vm_internal_pu | float64
210 | res_trafo3w | loading_percent | float64
211 | res_impedance | p_from_mw | float64
212 | res_impedance | q_from_mvar | float64
213 | res_impedance | p_to_mw | float64
214 | res_impedance | q_to_mvar | float64
215 | res_impedance | pl_mw | float64
216 | res_impedance | ql_mvar | float64
217 | res_impedance | i_from_ka | float64
218 | res_impedance | i_to_ka | float64
219 | res_ext_grid | p_mw | float64
220 | res_ext_grid | q_mvar | float64
221 | res_load | p_mw | float64
222 | res_load | q_mvar | float64
223 | res_sgen | p_mw | float64
224 | res_sgen | q_mvar | float64
225 | res_shunt | p_mw | float64
226 | res_shunt | q_mvar | float64
227 | res_shunt | vm_pu | float64
228 | res_gen | p_mw | float64
229 | res_gen | q_mvar | float64
230 | res_gen | va_degree | float64
231 | res_gen | vm_pu | float64
232 | res_xward | p_mw | float64
233 | res_xward | q_mvar | float64
234 | res_xward | vm_pu | float64
235 | res_xward | va_internal_degree | float64
236 | res_xward | vm_internal_pu | float64
237 | res_switch | i_ka | float64
238 | res_switch | loading_percent | float64