## parameters
| version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.10.1 | FALSE | FALSE |  | 50 | 1

## bus
| name | vn_kv | type | zone | in_service
0 | Trafostation_OS | 10 | b |  | TRUE
1 | main_busbar | 0.4 | b |  | TRUE
2 | bus_1_1 | 0.4 | b |  | TRUE
3 | bus_1_2 | 0.4 | b |  | TRUE
4 | bus_1_3 | 0.4 | b |  | TRUE
5 | bus_1_4 | 0.4 | b |  | TRUE
6 | bus_1_5 | 0.4 | b |  | TRUE
7 | bus_1_6 | 0.4 | b |  | TRUE
8 | bus_1_7 | 0.4 | b |  | TRUE
9 | bus_1_8 | 0.4 | b |  | TRUE
10 | bus_1_9 | 0.4 | b |  | TRUE
11 | bus_1_10 | 0.4 | b |  | TRUE
12 | bus_1_11 | 0.4 | b |  | TRUE
13 | bus_1_12 | 0.4 | b |  | TRUE
14 | bus_1_13 | 0.4 | b |  | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | line_1_1 | NFA2X 4x70 | 1 | 2 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
1 | line_1_2 | NFA2X 4x70 | 2 | 3 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
2 | line_1_3 | NFA2X 4x70 | 3 | 4 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
3 | line_1_4 | NFA2X 4x70 | 4 | 5 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
4 | line_1_5 | NFA2X 4x70 | 5 | 6 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
5 | line_1_6 | NFA2X 4x70 | 6 | 7 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
6 | line_1_7 | NFA2X 4x70 | 7 | 8 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
7 | line_1_8 | NFA2X 4x70 | 8 | 9 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
8 | line_1_9 | NFA2X 4x70 | 9 | 10 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
9 | line_1_10 | NFA2X 4x70 | 10 | 11 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
10 | line_1_11 | NFA2X 4x70 | 11 | 12 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
11 | line_1_12 | NFA2X 4x70 | 12 | 13 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE
12 | line_1_13 | NFA2X 4x70 | 13 | 14 | 0.021 | 0.443 | 0.069 | 0 | 0 | 0.27 | 1 | 1 | ol | TRUE

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
0

## shunt
bus | name | q_mvar | p_mw | vn_kv | step | max_step | in_service

## impedance
name | from_bus | to_bus | rft_pu | xft_pu | rtf_pu | xtf_pu | sn_mva | in_service

## dcline
name | from_bus | to_bus | p_mw | loss_percent | loss_mw | vm_from_pu | vm_to_pu | max_p_mw | min_q_from_mvar | min_q_to_mvar | max_q_from_mvar | max_q_to_mvar | in_service

## bus_geodata
| x | y | coords
0 | 0 | 0

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
NFA2X 4x70 | 0 | 0.443 | 0.069 | 0.27 | ol | 70
NAYY 4x50 | 670 | 0.6417 | 0.084823 | 0.141 | cs | 50
NAYY 4x150 | 830 | 0.2067 | 0.080425 | 0.275 | cs | 150
NAYY 4x185 | 830 | 0.165 | 0.080425 | 0.313 | cs | 185
NYY 4x35 | 0 | 0.52403 | 0.085137 | 0.156 | cs | 35

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | float64
49 | trafo | tap_min | float64
50 | trafo | tap_max | float64
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | float64
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool