## Summary
Summary
Line Overloaded
Line | Used Percentage
Voltage Violation in Bus
Bus | Voltage | Over/Under
Trafo Overloaded
Trafo | Used Percentage

## Demand
Demand
Step | Zone | Load Index | Bus Index | In service | Voltage Level [kV] | Active Power [MW] | Reactive Power [MVAr]
0 | --- | 0 | 20 | 1 | 110 | 38 | 6
0 | --- | 1 | 32 | 1 | 110 | 38 | 6
0 | --- | 2 | 33 | 1 | 110 | 38 | 6
0 | --- | 3 | 34 | 1 | 110 | 38 | 6
0 | --- | 4 | 35 | 1 | 110 | 38 | 6
0 | --- | 5 | 37 | 1 | 10 | 6 | 2
0 | --- | 6 | 36 | 1 | 20 | 16.3796 | 4
0 | --- | 7 | 38 | 1 | 10 | 0.4 | 0.1
0 | --- | 8 | 39 | 1 | 10 | 0.4 | 0.06
0 | --- | 9 | 40 | 1 | 10 | 0.4 | 0.06
0 | --- | 10 | 42 | 1 | 10 | 0.4 | 0.06
0 | --- | 11 | 43 | 1 | 10 | 0.4 | 0.06
0 | --- | 12 | 44 | 1 | 10 | 0.4 | 0.06
0 | --- | 13 | 45 | 1 | 0.4 | 0.1 | 0.1
0 | --- | 14 | 46 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 15 | 47 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 16 | 48 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 17 | 49 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 18 | 50 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 19 | 51 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 20 | 52 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 21 | 53 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 22 | 54 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 23 | 55 | 1 | 0.4 | 0.01 | 0.03
0 | --- | 24 | 56 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 0 | 20 | 1 | 110 | 38 | 6
1 | --- | 1 | 32 | 1 | 110 | 38 | 6
1 | --- | 2 | 33 | 1 | 110 | 38 | 6
1 | --- | 3 | 34 | 1 | 110 | 38 | 6
1 | --- | 4 | 35 | 1 | 110 | 38 | 6
1 | --- | 5 | 37 | 1 | 10 | 6 | 2
1 | --- | 6 | 36 | 1 | 20 | 16.3796 | 4
1 | --- | 7 | 38 | 1 | 10 | 0.4 | 0.1
1 | --- | 8 | 39 | 1 | 10 | 0.4 | 0.06
1 | --- | 9 | 40 | 1 | 10 | 0.4 | 0.06
1 | --- | 10 | 42 | 1 | 10 | 0.4 | 0.06
1 | --- | 11 | 43 | 1 | 10 | 0.4 | 0.06
1 | --- | 12 | 44 | 1 | 10 | 0.4 | 0.06
1 | --- | 13 | 45 | 1 | 0.4 | 0.1 | 0.1
1 | --- | 14 | 46 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 15 | 47 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 16 | 48 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 17 | 49 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 18 | 50 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 19 | 51 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 20 | 52 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 21 | 53 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 22 | 54 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 23 | 55 | 1 | 0.4 | 0.01 | 0.03
1 | --- | 24 | 56 | 1 | 0.4 | 0.01 | 0.03

## Generation
Generators
Step | Zone | Bus Index | Generator Index | Fuel | Technology | Voltage Level [kV] | Name | In Service | Voltage [p.u] | Maximum Active Power [MW] | Maximum Reactive Power [MVAr] | Minimum Active Power [MW] | Minimum Reactive Power [MVAr] | Active Power [MW] | Reactive Power [MVAr]
0 | --- | 35 | 0 | --- | --- | 110 | Gas turbine | 1 | 1.03 | --- |  | --- |  | 100 | 19.9222
1 | --- | 35 | 0 | --- | --- | 110 | Gas turbine | 1 | 1.03 | --- |  | --- |  | 100 | 19.9222
0 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1 | 600 | 450 | 0 | -450 | 466.51 | -38.2096
1 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1 | 40 | 30 | 0 | -30 |  | 30.7252
1 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1 | 520 | 390 | 0 | -390 |  | 194.6547
1 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1 | 600 | 450 | 0 | -450 |  | -38.2096
2 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
2 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
2 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
3 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
3 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
3 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
4 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
4 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
4 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
5 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
5 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
5 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
6 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
6 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
6 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
7 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
7 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
7 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
8 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
8 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
8 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
9 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
9 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
9 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1
10 | 1 | 0 | 0 | Coal | Steam Turbine | 230 | --- | 1 | 1
10 | 1 | 2 | 1 | NG | Gas Turbine | 230 | --- | 1 | 1
10 | 1 | 4 | 2 | Wind | Wind Turbine | 110 | --- | 1 | 1

## Generation01 (hidden)
Zone | (All)
Voltage Level [kV] | (All)
Sum of Active Power [MW] | Column Labels
| Coal | Coal Total | NG | NG Total | Wind | Wind Total | Grand Total
Row Labels | Steam Turbine |  | Gas Turbine |  | Wind Turbine
0 | 40 | 40 | 323.49 | 323.49 | 466.51 | 466.51 | 830
1 | 44 | 44 | 355.839 | 355.839 | 513.161 | 513.161 | 913
2 | 48.4 | 48.4 | 391.4229 | 391.4229 | 564.4771 | 564.4771 | 1004.3
3 | 53.24 | 53.24 | 430.5652 | 430.5652 | 620.9248 | 620.9248 | 1104.73
4 | 58.564 | 58.564 | 473.6217 | 473.6217 | 683.0173 | 683.0173 | 1215.203
5 | 64.4204 | 64.4204 | 520.9839 | 520.9839 | 751.319 | 751.319 | 1336.7233
6 | 70.8624 | 70.8624 | 573.0823 | 573.0823 | 826.4509 | 826.4509 | 1470.3956
7 | 77.9487 | 77.9487 | 630.3905 | 630.3905 | 909.096 | 909.096 | 1617.4352
8 | 85.7436 | 85.7436 | 693.4295 | 693.4295 | 1000.0056 | 1000.0056 | 1779.1787
9 | 94.3179 | 94.3179 | 762.7725 | 762.7725 | 1100.0062 | 1100.0062 | 1957.0966
10 | 103.7497 | 103.7497 | 839.0497 | 839.0497 | 1210.0068 | 1210.0068 | 2152.8062
Grand Total | 741.2467 | 741.2467 | 5994.6472 | 5994.6472 | 8644.9747 | 8644.9747 | 15380.8687

## Generation02 (hidden)
Row Labels | Sum of Active Power [MW]
Coal | 741.2467
Steam Turbine | 741.2467
230 | 741.2467
NG | 5994.6472
Gas Turbine | 5994.6472
230 | 5994.6472
Wind | 8644.9747
Wind Turbine | 8644.9747
110 | 8644.9747
Grand Total | 15380.8687

## Buses
Buses Parameters
Step | Bus Index | Zone | Name | Voltage Level [kV] | In Service | Voltage [p.u] | Voltage Phase [degree] | Active Power [MW] | Reactive Power [MVAr]
0 | 0 |  | Double Busbar 1 | 380 | 1 | 1.03 | 0 | -138.3884 | 7.3354
0 | 1 |  | Double Busbar 2 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 2 |  | Bus DB T0 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 3 |  | Bus DB T1 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 4 |  | Bus DB T2 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 5 |  | Bus DB T3 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 6 |  | Bus DB T4 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 7 |  | Bus DB T5 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 8 |  | Bus DB T6 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 9 |  | Bus DB T7 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 10 |  | Bus DB T8 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 11 |  | Bus DB T9 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 12 |  | Bus DB 1 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 13 |  | Bus DB 2 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 14 |  | Bus DB 3 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 15 |  | Bus DB 4 | 380 | 1 | 1.03 | 0 | 0 | 0
0 | 16 |  | Single Busbar | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 17 |  | Bus SB 1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 18 |  | Bus SB 2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 19 |  | Bus SB 3 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 20 |  | Bus SB 4 | 110 | 1 | 1.0323 | -1.9898 | 38 | 6
0 | 21 |  | Bus SB 5 | 110 | 1 | 1.0323 | -1.9898 | -0.48712 | -4
0 | 22 |  | Bus SB T1.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 23 |  | Bus SB T1.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 24 |  | Bus SB T2.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 25 |  | Bus SB T2.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 26 |  | Bus SB T3.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 27 |  | Bus SB T3.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 28 |  | Bus SB T4.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 29 |  | Bus SB T4.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 30 |  | Bus SB T5.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 31 |  | Bus SB T5.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
0 | 32 |  | Bus HV1 | 110 | 1 | 1.0217 | -4.1548 | 51.3537 | -1.327
0 | 33 |  | Bus HV2 | 110 | 1 | 1.0145 | -4.7793 | 38 | 6
0 | 34 |  | Bus HV3 | 110 | 1 | 1.0254 | -3.7509 | 64.9012 | -7.037
0 | 35 |  | Bus HV4 | 110 | 1 | 1.03 | -3.4657 | -62 | -13.9222
0 | 36 |  | Bus MV0 20kV | 20 | 1 | 1.0015 | -35.892 | 1.3796 | 1
0 | 37 |  | Bus MV0 | 10 | 1 | 1.0014 | -36.157 | 5.5 | 1.95
0 | 38 |  | Bus MV1 | 10 | 1 | 0.99746 | -36.187 | 0.4 | 0.1
0 | 39 |  | Bus MV2 | 10 | 1 | 0.99466 | -36.1888 | 0.4 | 0.06
0 | 40 |  | Bus MV3 | 10 | 1 | 0.99291 | -36.1565 | 0.4 | 0.06
0 | 41 |  | Bus MV4 | 10 | 1 | 0.99221 | -36.0899 | 0 | 0
0 | 42 |  | Bus MV5 | 10 | 1 | 1.0123 | -35.7004 | -1.6 | -0.04
0 | 43 |  | Bus MV6 | 10 | 1 | 1.0084 | -35.8517 | -0.1 | 0.06
0 | 44 |  | Bus MV7 | 10 | 1 | 1.0044 | -36.0205 | 0.4 | 0.06
0 | 45 |  | Bus LV0 | 0.4 | 1 | 0.94956 | 175.0723 | 0.1 | 0.1
0 | 46 |  | Bus LV1.1 | 0.4 | 1 | 0.94966 | 176.297 | -0.05 | 0.03
0 | 47 |  | Bus LV1.2 | 0.4 | 1 | 0.94543 | 177.1841 | 0.01 | 0.03
0 | 48 |  | Bus LV1.3 | 0.4 | 1 | 0.94384 | 177.8855 | -0.04 | 0.03
0 | 49 |  | Bus LV1.4 | 0.4 | 1 | 0.93885 | 178.2703 | 0.01 | 0.03
0 | 50 |  | Bus LV1.5 | 0.4 | 1 | 0.93636 | 178.4641 | 0.01 | 0.03
0 | 51 |  | Bus LV2.1 | 0.4 | 1 | 0.95503 | 177.4678 | 0.01 | 0.03
0 | 52 |  | Bus LV2.2 | 0.4 | 1 | 0.96561 | 179.546 | 0.01 | 0.03
0 | 53 |  | Bus LV2.3 | 0.4 | 1 | 1.0486 | -174.4757 | -0.04 | 0.03
0 | 54 |  | Bus LV2.4 | 0.4 | 1 | 1.0919 | -171.8361 | -0.04 | 0.03
0 | 55 |  | Bus LV2.2.1 | 0.4 | 1 | 1.0486 | -174.4757 | -0.04 | 0.03
0 | 56 |  | Bus LV2.2.2 | 0.4 | 1 | 1.0919 | -171.8361 | -0.04 | 0.03
1 | 0 |  | Double Busbar 1 | 380 | 1 | 1.03 | 0 | -138.3884 | 7.3354
1 | 1 |  | Double Busbar 2 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 2 |  | Bus DB T0 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 3 |  | Bus DB T1 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 4 |  | Bus DB T2 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 5 |  | Bus DB T3 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 6 |  | Bus DB T4 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 7 |  | Bus DB T5 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 8 |  | Bus DB T6 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 9 |  | Bus DB T7 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 10 |  | Bus DB T8 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 11 |  | Bus DB T9 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 12 |  | Bus DB 1 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 13 |  | Bus DB 2 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 14 |  | Bus DB 3 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 15 |  | Bus DB 4 | 380 | 1 | 1.03 | 0 | 0 | 0
1 | 16 |  | Single Busbar | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 17 |  | Bus SB 1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 18 |  | Bus SB 2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 19 |  | Bus SB 3 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 20 |  | Bus SB 4 | 110 | 1 | 1.0323 | -1.9898 | 38 | 6
1 | 21 |  | Bus SB 5 | 110 | 1 | 1.0323 | -1.9898 | -0.48712 | -4
1 | 22 |  | Bus SB T1.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 23 |  | Bus SB T1.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 24 |  | Bus SB T2.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 25 |  | Bus SB T2.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 26 |  | Bus SB T3.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 27 |  | Bus SB T3.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 28 |  | Bus SB T4.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 29 |  | Bus SB T4.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 30 |  | Bus SB T5.1 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 31 |  | Bus SB T5.2 | 110 | 1 | 1.0323 | -1.9898 | 0 | 0
1 | 32 |  | Bus HV1 | 110 | 1 | 1.0217 | -4.1548 | 51.3537 | -1.327
1 | 33 |  | Bus HV2 | 110 | 1 | 1.0145 | -4.7793 | 38 | 6
1 | 34 |  | Bus HV3 | 110 | 1 | 1.0254 | -3.7509 | 64.9012 | -7.037
1 | 35 |  | Bus HV4 | 110 | 1 | 1.03 | -3.4657 | -62 | -13.9222
1 | 36 |  | Bus MV0 20kV | 20 | 1 | 1.0015 | -35.892 | 1.3796 | 1
1 | 37 |  | Bus MV0 | 10 | 1 | 1.0014 | -36.157 | 5.5 | 1.95
1 | 38 |  | Bus MV1 | 10 | 1 | 0.99746 | -36.187 | 0.4 | 0.1
1 | 39 |  | Bus MV2 | 10 | 1 | 0.99466 | -36.1888 | 0.4 | 0.06
1 | 40 |  | Bus MV3 | 10 | 1 | 0.99291 | -36.1565 | 0.4 | 0.06
1 | 41 |  | Bus MV4 | 10 | 1 | 0.99221 | -36.0899 | 0 | 0
1 | 42 |  | Bus MV5 | 10 | 1 | 1.0123 | -35.7004 | -1.6 | -0.04
1 | 43 |  | Bus MV6 | 10 | 1 | 1.0084 | -35.8517 | -0.1 | 0.06
1 | 44 |  | Bus MV7 | 10 | 1 | 1.0044 | -36.0205 | 0.4 | 0.06
1 | 45 |  | Bus LV0 | 0.4 | 1 | 0.94956 | 175.0723 | 0.1 | 0.1
1 | 46 |  | Bus LV1.1 | 0.4 | 1 | 0.94966 | 176.297 | -0.05 | 0.03
1 | 47 |  | Bus LV1.2 | 0.4 | 1 | 0.94543 | 177.1841 | 0.01 | 0.03
1 | 48 |  | Bus LV1.3 | 0.4 | 1 | 0.94384 | 177.8855 | -0.04 | 0.03
1 | 49 |  | Bus LV1.4 | 0.4 | 1 | 0.93885 | 178.2703 | 0.01 | 0.03
1 | 50 |  | Bus LV1.5 | 0.4 | 1 | 0.93636 | 178.4641 | 0.01 | 0.03
1 | 51 |  | Bus LV2.1 | 0.4 | 1 | 0.95503 | 177.4678 | 0.01 | 0.03
1 | 52 |  | Bus LV2.2 | 0.4 | 1 | 0.96561 | 179.546 | 0.01 | 0.03
1 | 53 |  | Bus LV2.3 | 0.4 | 1 | 1.0486 | -174.4757 | -0.04 | 0.03
1 | 54 |  | Bus LV2.4 | 0.4 | 1 | 1.0919 | -171.8361 | -0.04 | 0.03
1 | 55 |  | Bus LV2.2.1 | 0.4 | 1 | 1.0486 | -174.4757 | -0.04 | 0.03
1 | 56 |  | Bus LV2.2.2 | 0.4 | 1 | 1.0919 | -171.8361 | -0.04 | 0.03

## Lines01 (hidden)
Zone | (All)
Voltage Level [kV] | (All)
Row Labels | Max of Loading Percent [%] | Average of Loading Percent [%] | Min of Loading Percent [%]2
0 | 100.1732 | 27.1434 | 7.2341e-05
1 | 110.1905 | 29.8577 | 7.9575e-05
2 | 121.2095 | 32.8435 | 8.7532e-05
3 | 133.3305 | 36.1278 | 9.6285e-05
4 | 146.6635 | 39.7406 | 0.00010591
5 | 161.3299 | 43.7147 | 0.00011651
6 | 177.4629 | 48.0861 | 0.00012816
7 | 195.2092 | 52.8948 | 0.00014097
8 | 214.7301 | 58.1842 | 0.00015507
9 | 236.2031 | 64.0027 | 0.00017058
10 | 259.8234 | 70.4029 | 0.00018763
Grand Total | 259.8234 | 45.7271 | 7.2341e-05

## Lines02 (hidden)
Zone | (All)
Voltage Level [kV] | (All)
Row Labels | Sum of Losses [MW]
0 | 5.0272
1 | 5.5299
2 | 6.0829
3 | 6.6912
4 | 7.3603
5 | 8.0963
6 | 8.906
7 | 9.7966
8 | 10.7762
9 | 11.8538
10 | 13.0392
Grand Total | 93.1595

## Lines
Tranmission and Distribution Lines
Step | Zone | Line Index | Voltage Level [kV] | Name | From bus | To Bus | In service | Length [km] | Maximum Current [kA] | Maximum Loading [%] | Number of Lines in Parallel | Std. Type | From Bus Act. Power [MW] | From Bus Raact. Power [MVAr] | To Bus Act. Power [MW] | To Bus Raact. Power [MVAr] | Losses [MW] | Losses [MVAr] | Loading Percent [%]
0 | --- | 0 | 110 | HV Line1 | 18 | 32 | 1 | 30 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | 38.7963 | -4.0437 | -38.2416 | 4.3976 | 0.5547 | 0.35388 | 37.0718
0 | --- | 1 | 110 | HV Line2 | 32 | 33 | 1 | 20 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | 18.6295 | 3.5761 | -18.5393 | -4.0401 | 0.090163 | -0.46392 | 18.3489
0 | --- | 2 | 110 | HV Line3 | 33 | 35 | 1 | 30 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -26.2287 | -5.7942 | 26.4996 | 5.4352 | 0.27089 | -0.35903 | 25.9756
0 | --- | 3 | 110 | HV Line4 | 32 | 35 | 1 | 15 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -27.8722 | -6.234 | 28.0238 | 6.0919 | 0.15159 | -0.14211 | 27.4242
0 | --- | 4 | 110 | HV Line5 | 34 | 35 | 1 | 25 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -7.457 | -3.2286 | 7.4766 | 2.3952 | 0.019568 | -0.83343 | 7.7747
0 | --- | 5 | 110 | HV Line6 | 19 | 34 | 1 | 30 | 0.535 | --- | 2 | 184-AL1/30-ST1A 110.0 | 62.043 | -10.1189 | -61.3244 | 9.8239 | 0.71852 | -0.29501 | 29.8724
0 | --- | 6 | 10 | MV Line1 | 37 | 38 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.1688 | 0.62642 | -1.1645 | -0.63618 | 0.0042543 | -0.0097585 | 21.2173
0 | --- | 7 | 10 | MV Line2 | 38 | 39 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 0.76451 | 0.53618 | -0.76237 | -0.5474 | 0.0021333 | -0.011213 | 15.0491
0 | --- | 8 | 10 | MV Line3 | 39 | 40 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 0.36237 | 0.4874 | -0.36146 | -0.49944 | 0.00091566 | -0.01204 | 9.903
0 | --- | 9 | 10 | MV Line4 | 40 | 41 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | -0.038541 | 0.43944 | 0.039032 | -0.45175 | 0.00049042 | -0.012318 | 7.2886
0 | --- | 10 | 10 | MV Line5 | 41 | 42 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 9.8375e-08 | -0.012665 | -3.4183e-14 | 2.4918e-14 | 9.8375e-08 | -0.012665 | 0.20358
0 | --- | 11 | 10 | MV Line6 | 42 | 43 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.6 | 0.04 | -1.594 | -0.048745 | 0.0060379 | -0.0087454 | 25.2213
0 | --- | 12 | 10 | MV Line7 | 43 | 44 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.694 | -0.011255 | -1.6871 | 0.0031766 | 0.0068146 | -0.008078 | 26.7916
0 | --- | 13 | 10 | MV Line8 | 37 | 44 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | -1.2832 | 0.053125 | 1.2871 | -0.063177 | 0.0039739 | -0.010051 | 20.4636
0 | --- | 14 | 0.4 | LV Line1.1 | 45 | 46 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.053194 | 0.15242 | 0.056445 | -0.15126 | 0.0032515 | 0.0011551 | 101.3982
0 | --- | 15 | 0.4 | LV Line1.2 | 46 | 47 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.006445 | 0.12126 | 0.0082845 | -0.12061 | 0.0018394 | 0.00065306 | 76.2658
0 | --- | 16 | 0.4 | LV Line1.3 | 47 | 48 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.018284 | 0.090607 | 0.01936 | -0.090226 | 0.0010754 | 0.00038141 | 58.3135
0 | --- | 17 | 0.4 | LV Line1.4 | 48 | 49 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | 0.02064 | 0.060226 | -0.020128 | -0.060045 | 0.00051186 | 0.00018105 | 40.2316
0 | --- | 18 | 0.4 | LV Line1.6 | 49 | 50 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | 0.010128 | 0.030045 | -0.01 | -0.03 | 0.00012831 | 4.4687e-05 | 20.1428
0 | --- | 19 | 0.4 | LV Line2.1 | 45 | 51 | 1 | 0.12 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.094043 | 0.19118 | 0.10254 | -0.18816 | 0.0084958 | 0.0030193 | 133.8276
0 | --- | 20 | 0.4 | LV Line2.2 | 51 | 52 | 1 | 0.12 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.11254 | 0.15816 | 0.11951 | -0.15569 | 0.0069715 | 0.0024773 | 121.2294
0 | --- | 21 | 0.4 | LV Line2.3 | 52 | 53 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.064755 | 0.062843 | 0.077048 | -0.06055 | 0.012293 | 0.0022923 | 128.4591
0 | --- | 22 | 0.4 | LV Line2.4 | 53 | 54 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.037048 | 0.03055 | 0.04 | -0.03 | 0.0029519 | 0.00055038 | 62.9486
0 | --- | 23 | 0.4 | LV Line2.2.1 | 52 | 55 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.064755 | 0.062843 | 0.077048 | -0.06055 | 0.012293 | 0.0022923 | 128.4591
0 | --- | 24 | 0.4 | LV Line2.2.2 | 55 | 56 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.037048 | 0.03055 | 0.04 | -0.03 | 0.0029519 | 0.00055038 | 62.9486
1 | --- | 0 | 110 | HV Line1 | 18 | 32 | 1 | 30 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | 38.7963 | -4.0437 | -38.2416 | 4.3976 | 0.5547 | 0.35388 | 37.0718
1 | --- | 1 | 110 | HV Line2 | 32 | 33 | 1 | 20 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | 18.6295 | 3.5761 | -18.5393 | -4.0401 | 0.090163 | -0.46392 | 18.3489
1 | --- | 2 | 110 | HV Line3 | 33 | 35 | 1 | 30 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -26.2287 | -5.7942 | 26.4996 | 5.4352 | 0.27089 | -0.35903 | 25.9756
1 | --- | 3 | 110 | HV Line4 | 32 | 35 | 1 | 15 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -27.8722 | -6.234 | 28.0238 | 6.0919 | 0.15159 | -0.14211 | 27.4242
1 | --- | 4 | 110 | HV Line5 | 34 | 35 | 1 | 25 | 0.535 | --- | 1 | 184-AL1/30-ST1A 110.0 | -7.457 | -3.2286 | 7.4766 | 2.3952 | 0.019568 | -0.83343 | 7.7747
1 | --- | 5 | 110 | HV Line6 | 19 | 34 | 1 | 30 | 0.535 | --- | 2 | 184-AL1/30-ST1A 110.0 | 62.043 | -10.1189 | -61.3244 | 9.8239 | 0.71852 | -0.29501 | 29.8724
1 | --- | 6 | 10 | MV Line1 | 37 | 38 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.1688 | 0.62642 | -1.1645 | -0.63618 | 0.0042543 | -0.0097585 | 21.2173
1 | --- | 7 | 10 | MV Line2 | 38 | 39 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 0.76451 | 0.53618 | -0.76237 | -0.5474 | 0.0021333 | -0.011213 | 15.0491
1 | --- | 8 | 10 | MV Line3 | 39 | 40 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 0.36237 | 0.4874 | -0.36146 | -0.49944 | 0.00091566 | -0.01204 | 9.903
1 | --- | 9 | 10 | MV Line4 | 40 | 41 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | -0.038541 | 0.43944 | 0.039032 | -0.45175 | 0.00049042 | -0.012318 | 7.2886
1 | --- | 10 | 10 | MV Line5 | 41 | 42 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 9.8375e-08 | -0.012665 | -3.4183e-14 | 2.4918e-14 | 9.8375e-08 | -0.012665 | 0.20358
1 | --- | 11 | 10 | MV Line6 | 42 | 43 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.6 | 0.04 | -1.594 | -0.048745 | 0.0060379 | -0.0087454 | 25.2213
1 | --- | 12 | 10 | MV Line7 | 43 | 44 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | 1.694 | -0.011255 | -1.6871 | 0.0031766 | 0.0068146 | -0.008078 | 26.7916
1 | --- | 13 | 10 | MV Line8 | 37 | 44 | 1 | 1.5 | 0.362 | --- | 1 | NA2XS2Y 1x185 RM/25 12/20 kV | -1.2832 | 0.053125 | 1.2871 | -0.063177 | 0.0039739 | -0.010051 | 20.4636
1 | --- | 14 | 0.4 | LV Line1.1 | 45 | 46 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.053194 | 0.15242 | 0.056445 | -0.15126 | 0.0032515 | 0.0011551 | 101.3982
1 | --- | 15 | 0.4 | LV Line1.2 | 46 | 47 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.006445 | 0.12126 | 0.0082845 | -0.12061 | 0.0018394 | 0.00065306 | 76.2658
1 | --- | 16 | 0.4 | LV Line1.3 | 47 | 48 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.018284 | 0.090607 | 0.01936 | -0.090226 | 0.0010754 | 0.00038141 | 58.3135
1 | --- | 17 | 0.4 | LV Line1.4 | 48 | 49 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | 0.02064 | 0.060226 | -0.020128 | -0.060045 | 0.00051186 | 0.00018105 | 40.2316
1 | --- | 18 | 0.4 | LV Line1.6 | 49 | 50 | 1 | 0.08 | 0.242 | --- | 1 | NAYY 4x120 SE | 0.010128 | 0.030045 | -0.01 | -0.03 | 0.00012831 | 4.4687e-05 | 20.1428
1 | --- | 19 | 0.4 | LV Line2.1 | 45 | 51 | 1 | 0.12 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.094043 | 0.19118 | 0.10254 | -0.18816 | 0.0084958 | 0.0030193 | 133.8276
1 | --- | 20 | 0.4 | LV Line2.2 | 51 | 52 | 1 | 0.12 | 0.242 | --- | 1 | NAYY 4x120 SE | -0.11254 | 0.15816 | 0.11951 | -0.15569 | 0.0069715 | 0.0024773 | 121.2294
1 | --- | 21 | 0.4 | LV Line2.3 | 52 | 53 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.064755 | 0.062843 | 0.077048 | -0.06055 | 0.012293 | 0.0022923 | 128.4591
1 | --- | 22 | 0.4 | LV Line2.4 | 53 | 54 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.037048 | 0.03055 | 0.04 | -0.03 | 0.0029519 | 0.00055038 | 62.9486
1 | --- | 23 | 0.4 | LV Line2.2.1 | 52 | 55 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.064755 | 0.062843 | 0.077048 | -0.06055 | 0.012293 | 0.0022923 | 128.4591
1 | --- | 24 | 0.4 | LV Line2.2.2 | 55 | 56 | 1 | 0.12 | 0.105 | --- | 1 | 15-AL1/3-ST1A 0.4 | -0.037048 | 0.03055 | 0.04 | -0.03 | 0.0029519 | 0.00055038 | 62.9486
| 1 | 2 | 230 | --- | 0 | 4 | 1 | 1 | 99999 | 100 | 1 | --- | -866.8688 | 120.6471 | 873.6603 | -53.4058 |  | 67.2414
| 1 | 3 | 230 | --- | 1 | 2 | 1 | 1 | 99999 | 100 | 1 | --- | -1076.4288 | 150.1464 | 1084.9121 | -65.9877 |  | 84.1587
| 1 | 4 | 230 | --- | 2 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -1285.9888 | 179.6456 | 1296.1638 | -78.5696 |  | 101.076
| 1 | 5 | 230 | --- | 3 | 4 | 1 | 1 | 0.60245 | 100 | 1 | --- | -1495.5489 | 209.1449 | 1507.4156 | -91.1515 |  | 117.9934
| 1 | 0 | 110 | --- | 0 | 1 | 1 | 1 | 1.0041 | 100 | 1 | --- | -1705.1089 | 238.6442 | 1718.6674 | -103.7335 |  | 134.9107
| 1 | 1 | 230 | --- | 0 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -1914.6689 | 268.1434 | 1929.9191 | -116.3154 |  | 151.828
| 1 | 2 | 230 | --- | 0 | 4 | 1 | 1 | 99999 | 100 | 1 | --- | -2124.229 | 297.6427 | 2141.1709 | -128.8973 |  | 168.7453
| 1 | 3 | 230 | --- | 1 | 2 | 1 | 1 | 99999 | 100 | 1 | --- | -2333.789 | 327.1419 | 2352.4227 | -141.4793 |  | 185.6627
| 1 | 4 | 230 | --- | 2 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -2543.349 | 356.6412 | 2563.6744 | -154.0612 |  | 202.58
| 1 | 5 | 230 | --- | 3 | 4 | 1 | 1 | 0.60245 | 100 | 1 | --- | -2752.9091 | 386.1404 | 2774.9262 | -166.6431 |  | 219.4973
| 1 | 0 | 110 | --- | 0 | 1 | 1 | 1 | 1.0041 | 100 | 1 | --- | -2962.4691 | 415.6397 | 2986.178 | -179.225 |  | 236.4146
| 1 | 1 | 230 | --- | 0 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -3172.0291 | 445.1389 | 3197.4297 | -191.807 |  | 253.332
| 1 | 2 | 230 | --- | 0 | 4 | 1 | 1 | 99999 | 100 | 1 | --- | -3381.5891 | 474.6382 | 3408.6815 | -204.3889 |  | 270.2493
| 1 | 3 | 230 | --- | 1 | 2 | 1 | 1 | 99999 | 100 | 1 | --- | -3591.1492 | 504.1374 | 3619.9332 | -216.9708 |  | 287.1666
| 1 | 4 | 230 | --- | 2 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -3800.7092 | 533.6367 | 3831.185 | -229.5527 |  | 304.0839
| 1 | 5 | 230 | --- | 3 | 4 | 1 | 1 | 0.60245 | 100 | 1 | --- | -4010.2692 | 563.1359 | 4042.4368 | -242.1347 |  | 321.0013

## Trafos
Transformers
Time Step | Zone | Trafo Index | Name | Std Type | HV Bus | LV Bus | High Voltage Side [kV] | Low Voltage Side [kV] | FE Losses [kW] | Shift Degree | Tap Position | Number of Trafos in Parallel | In Service | HV Act. Power [MW] | HV React. Power [MVAr] | LV Act. Power [MW] | LV React. Power [MVAr] | Losses [MW] | Losses [MVAr] | Loading Percent [%]
0 | --- | 0 | EHV-HV-Trafo | --- | 13 | 17 | 380 | 110 | 0 | 0 |  | 1 | 1 | 138.3884 | -7.3354 | -138.3521 | 12.1626 | 0.036205 | 4.8272 | 44.8487
0 | --- | 1 | MV-LV-Trafo | --- | 41 | 45 | 10 | 0.4 | 0.95 | 150 | 0 | 1 | 1 | -0.039032 | 0.46442 | 0.047237 | -0.4436 | 0.0082051 | 0.020821 | 117.4502
1 | --- | 0 | EHV-HV-Trafo | --- | 13 | 17 | 380 | 110 | 0 | 0 |  | 1 | 1 | 138.3884 | -7.3354 | -138.3521 | 12.1626 | 0.036205 | 4.8272 | 44.8487
1 | --- | 1 | MV-LV-Trafo | --- | 41 | 45 | 10 | 0.4 | 0.95 | 150 | 0 | 1 | 1 | -0.039032 | 0.46442 | 0.047237 | -0.4436 | 0.0082051 | 0.020821 | 117.4502