## Demand
Demand
Zone | Load Index | Bus Index | In service | Voltage Level [kV] | Active Power [MW] | Reactive Power [MVAr]
1 | 0 | 1 | 1 | 230 | 300 | 98.61
1 | 1 | 2 | 1 | 230 | 300 | 98.61
1 | 2 | 3 | 1 | 230 | 400 | 131.47

## Generation
Conventional Generators | [12 empty] | Renewable Energies
Zone | Bus Index | Generator Index | Voltage Level [kV] | Name | In Service | Voltage [p.u] | Maximum Active Power [MW] | Maximum Reactive Power [MVAr] | Minimum Active Power [MW] | Minimum Reactive Power [MVAr] | Active Power [MW] | Reactive Power [MVAr] | Zone | Bus Index | Generator Index | Voltage Level [kV] | Name | In Service | Voltage [p.u] | Maximum Active Power [MW] | Maximum Reactive Power [MVAr] | Minimum Active Power [MW] | Minimum Reactive Power [MVAr] | Active Power [MW] | Reactive Power [MVAr]
1 | 0 | 0 | 230 | --- | 1 | 1 | 40 | 30 | 0 | -30 | 40 | 30.7252
1 | 2 | 1 | 230 | --- | 1 | 1 | 520 | 390 | 0 | -390 | 323.49 | 194.6547
1 | 4 | 2 | 230 | --- | 1 | 1 | 600 | 450 | 0 | -450 | 466.51 | -38.2096

## Buses
Buses Parameters
Bus Index | Zone | Name | Voltage Level [kV] | In Service | Voltage [p.u] | Voltage Phase [degree] | Active Power [MW] | Reactive Power [MVAr]
0 | 1 | 0 | 230 | 1 | 1 | 3.2734 | -210 | -30.7252
1 | 1 | 1 | 230 | 1 | 0.98926 | -0.75927 | 300 | 98.61
2 | 1 | 2 | 230 | 1 | 1 | -0.49226 | -23.49 | -96.0447
3 | 1 | 3 | 230 | 1 | 1 | 0 | 394.9728 | -52.6529
4 | 1 | 4 | 230 | 1 | 1 | 4.112 | -466.51 | 38.2096

## Lines
Tranmission and Distribution Lines
Zone | Line Index | Voltage Level [kV] | Name | From bus | To Bus | In service | Length [km] | Maximum Current [kA] | Maximum Loading [%] | Number of Lines in Parallel | Std. Type | From Bus Act. Power [MW] | From Bus Raact. Power [MVAr] | To Bus Act. Power [MW] | To Bus Raact. Power [MVAr] | Losses [MW] | Losses [MVAr] | Loading Percent [%]
1 | 0 | 230 | --- | 0 | 1 | 1 | 1 | 1.0041 | 100 | 1 | --- | 249.7734 | 21.5991 | -248.0068 | -4.6374 | 1.7666 | 16.9617 | 62.6857
1 | 1 | 230 | --- | 0 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | 186.5001 | -13.6121 | -185.4374 | 23.5816 | 1.0627 | 9.9695 | 0.00046941
1 | 2 | 230 | --- | 0 | 4 | 1 | 1 | 99999 | 100 | 1 | --- | -226.2735 | 22.7382 | 226.605 | -22.5496 | 0.33146 | 0.18858 | 0.00057164
1 | 3 | 230 | --- | 1 | 2 | 1 | 1 | 99999 | 100 | 1 | --- | -51.9932 | -93.9726 | 52.1187 | 93.3946 | 0.12542 | -0.57804 | 0.00027252
1 | 4 | 230 | --- | 2 | 3 | 1 | 1 | 99999 | 100 | 1 | --- | -28.6287 | 2.6501 | 28.6533 | -3.0781 | 0.024607 | -0.42793 | 7.2341e-05
1 | 5 | 230 | --- | 3 | 4 | 1 | 1 | 0.60245 | 100 | 1 | --- | -238.1887 | 32.1494 | 239.905 | -15.66 | 1.7163 | 16.4894 | 100.1732

## Trafos
Transformers
Zone | Line Index | Voltage Level [kV] | Name | From bus | To Bus | In service | Length [km] | Maximum Current [kA] | Maximum Loading [%] | Number of Lines in Parallel | Std. Type | From Bus Act. Power [MW] | From Bus Raact. Power [MVAr] | To Bus Act. Power [MW] | To Bus Raact. Power [MVAr] | Losses [MW] | Losses [MVAr] | Loading Percent [%]